
|  |  |
| --- | --- |
| **Project Name: Bunning Store – Berri SA** | **Date:April 16** |
| **Project No… DF/PD685** | **Sheet 7 of 9** |

|  |
| --- |
| **Inline Exhaust Fan** |
| **System: EF - 03** |
| **Location: Timber Trade Sales** |
| **Tested By: Scott Mcgahey** |
| **Witnessed Josh Edwards** |



**IN-LINE FAN – DIRECT DRIVE**

Make Fantech

Model AP0806GP6/31

Rated kW 2.42KW

Speed 16 R/S

FLC/ Start (A): 5.72/32.76

Voltage: 415V – 3 Phase

Specified Duty: 5400L/S (900L/S per 1000 x 600 grille)

Air Flow Results 53 886

54 891

55 906

56 912

57 902

58 907

5404